This section is based on the products of Garaventa Lift, which is located at:

United States

P.O.  Box 1769

Blaine, WA 98231-1769

Canada

7505 134 A St.

Surrey, BC V3A 3WB

Toll Free: 800-663-6556

Tel:  (604) 594-0422

Fax:  (604) 594-9915

Email: productinfo@garaventalift.com

Web: www.garaventalift.com

[click Here] for additional information.

Garaventa Lift is an international company specializing in the manufacturing of wheelchair lifts and elevators. A world leader in the accessibility industry with a reputation for reliability, safety and innovation, Garaventa Lift has over 50,000 installations worldwide.

The Genesis Staage is a portable vertical wheelchair lift which provides temporary accessibility.

IMPORTANT: PLEASE CONTACT GARAVENTA LIFT FOR DEALER ASSISTANCE IN DEVELOPING LOCATION-SPECIFIC DESIGN SPECIFICATIONS. THIS PRODUCT MAY NOT BE SUITABLE FOR PROVIDING CODE-COMPLIANT ACCESSIBILITY.

GARAVENTA GENESIS STAAGE VERTICAL LIFT

PORTABLE MODEL DESIGN SPECIFICATIONS

# VERTICAL LIFT DESIGN SPECIFICATIONS

PART 1 GENERAL

  - DESCRIPTION OF PRODUCT

- The Genesis STAAGE – manufactured by Garaventa Lift – is a portable vertical platform lift for indoor/outdoor use consisting of a machine tower with a lifting platform, selected and dimensioned to provide building access for mobility impaired persons.

  - MANUFACTURER

Supplier with not less than ten (10) years experience in design, fabrication, and installation of specialized equipment for mobility impaired persons.

# DEALER/DISTRIBUTOR

- Must be a contractor licensed to provide equipment of this scope, with evidence of experience with this equipment. The authorized Garaventa Lift dealer/distributor must also employ competent personnel, maintain an adequate stock of replacement parts, have qualified people available to ensure fulfillment of maintenance and call-back service without unreasonable loss of time in reaching the site.

  - WARRANTY

- Warranty: Manufacturer shall warrant the Genesis STAAGE vertical lift materials and workmanship for two years.

- Extended Warranty (optional): Manufacturer shall warrant the Genesis STAAGE vertical lift materials and workmanship for up to five (5) additional years following completion of the delivery and execution of a Preventive Maintenance Agreement.

  - MAINTENANCE

- The cost of renewals or repairs caused by reason of negligence, misuse, or accidents beyond the control of the lift contractor shall not be the responsibility of the contractor.

- If call-back service is required between regular inspections, and is necessitated by defects, which are not covered by the warranty, this contractor will be reimbursed by the owner. Call-back service necessitated by defects, which are covered by the warranty, shall be provided without charge.

# PART 2  PRODUCT

This section covers the supply and installation of one vertical platform lift system. (Optional equipment and selection items are underlined.)

  - MANUFACTURER/EQUIPMENT

Lift manufactured by Garaventa Lift distributed by

_____________________________ configured as follows:

Model Type: 			STAAGE

Platform Size: 			864mm x 1385mm (34” x 54 ½”) Standard

864mm x 1334mm (34” x 52 ½”) If optional lower landing platform gate selected

Machine Tower: 		Custom aluminum extrusion – anodized champagne finish.

Portable Base Frame: 	Structural steel tubing frame with 3 heavy-duty castor wheels.  Front castor wheel is to be mounted on a jack.

Platform Side Wall Panels: 	16 gauge galvanized steel sheet panels.

Platform and Access Ramp: 	12 gauge formed, galvanized steel plates; slip resistant surfaces. The access ramp is an automatic folding ramp design.

Coatings/Surfacing: 	Finished in process consisting of alkaline detergent wash, clear water rinse, iron phosphate coating, clear water rinse, non-chromate rinse, and baked polyester electrostatically applied for indoor/outdoor use.

Capacity:          		Maximum 340kg. (750lbs) Operating load.

Drive Style: 			Self-lubricating acme drive nut and screw gear belt pulley.

Emergency Operation: 	Manual lowering device capable of raising or lowering platform in event of power failure.

Lifting Height: 			Externally adjustable up to a maximum of 44”

Travel Speed: 			3 meters/minute (10 feet per minute)

Motor: 	2 H.P Motor:

Power: 	120VAC mains power input.  10’ power cord and wall plug included by manufacturer.

Panel Color: 			Satin Grey (fine texture)

(Optional RAL colors are available from Manufacturer)

Platform Gates:  	Upper Landing Gate 1220mm (48”) high, equipped with self closer and interlock.

Lower landing platform gate 1100mm (43”) high, equipped with self closer and interlock.

Side Wall Panels: 		1100mm (43”) on platform.

Safety Devices:

- Grounded electrical system with upper, lower, and final limit switches and 24VDC operating controls.

- Non-slip platform and access ramp surfaces.

- Operation lock out key switch on lower landing call station

- Mechanical interlock with electrical switch monitors the door in the closed position to ensure that the latch is engaged

- Integral safety nut assembly with safety switch.

- Emergency stop switch shuts off power to lift and activates audio alarm.

  - APPLICABLE STANDARDS

- All electrical circuits, structural components and safety devices shall be designed and manufactured in accordance with the following standards:

- ASME A18.1 “Safety Standard for Platform Lifts and Stairway Chairlifts.”

* If equipped with lower landing platform gate.

- ANSI A117.1 “Providing Accessibility and Usability for Physically Handicapped People.”

- CAN/CSA-B44.1-96/ASME A17.5 Electrical Code for Elevating Devices.